Delegations will find in the Annex comments received from Greece on the abovementioned proposal.

ANNEX

GREECE

The proposed ELVs for the islands regarding new installations (see the proposed amendments in Annex II that follows) that are not interconnected to the mainland have as a source of inspiration the following:

- Ft.5 of Table 2 (NOx emissions from diesel engines) comes directly from GP (that, in this case, refers only to new installations and not existing ones) for a 10 year transitional period (“… a transition period of 10 years after the entry into force of the present Protocol for a Party may be applied …”). After this 10 years period the GP provides for 225 mg/Nm3 for diesel engines 5-20 MW (for HFO) and 190 mg/Nm3 for those diesel engines >20 MW.

- Ft.7 of Tables 1 and 2 (that refer to PM) and ft.6 of Table 2 (that refers to NOx from gas turbines that operate with diesel oil) are based on the practical experience of the Greek authorities.

- The other proposed ELVs for SIS/MIS (i.e. ft.5 and 6 of Table 1 and ft.4 of Table 2) come directly from the existing BREFs (i.e. as is the case for the other footnotes that have been included and do not refer to the non interconnected islands).

Regarding existing installations, for reasons of simplicity, we propose to apply the same ELVs but 5 years later than the “normal” application date, i.e. 2025 instead of 2030.

Furthermore, the definition of SIS/MIS may need to be adjusted in order to be appropriate for this Directive.

ANNEX II

Emission limit values referred to in Article 5(1)

…

…

…

Part 2

Emission limit values for new medium combustion plants

1. Emission limit values (mg/Nm³) for medium combustion plants other than engines and gas turbines

| Pollutant | Solid biomass | Other solid fuels | Liquid fuels other than heavy fuel oil | Heavy fuel oil | Natural gas | Gaseous fuels other than natural gas |
| --- | --- | --- | --- | --- | --- | --- |
| SO2 | 200 | 400 | 170 | 350(5) | - | 35(3) (4) |
| NOX | 300 | 300 | 200 | 300(6) | 100 | 200 |
| Particulate matter | 20(1) | 20 | 20(2) | 20(7) | - | - |

(1)	25 mg/Nm3 for plants with a thermal input below or equal to 5 MW

(2)	30 mg/Nm3 in case of recovery boilers in installations for Kraft pulp production

(3)	45 mg/Nm3 in case of refinery fuel gas

(4)	400 mg/Nm³ in case of low calorific gases from coke oven and 200 mg/Nm³ in case of low calorific gases from blast furnace (iron and steel industry)

[(5)	1700 mg/Nm³ in case of boilers in Small Isolated Systems (SIS) and Micro Isolated Systems (MIS)* as defined in Directive 2009/72/EC

Comment: According to BREF LCP 2006, par. 6.1.10.1.2 Control of emissions to air from liquid fuel-fired boilers / Abatement of SO2 emissions, p. 353:

“Switching to low-sulphur oil might be a technique which can make a significant contribution to SO2 emissions reduction. A decrease of 0,5% in the oil sulphur content leads to a decrease in the emission value by about 800 mg/Nm3 at 3% oxygen in the waste gas.”

The ELV of 1700 mg/Nm3 corresponds stoichiometrically to low sulphur HFO (1% w.w), i.e. the minimum content that is available in the Greek market.

(6)	450 mg/Nm³ for HFO firing with max. 0.3 % N in fuel oil and 360 mg/Nm³ for HFO firing with max. 0.2 % N in fuel oil in case of boilers in SIS and MIS as defined in Directive 2009/72/EC

Comment: According to BREF LCP 2006, par6.5.3.4 BAT for liquid fuel-fired boilers / BAT-AELs for NOx emissions, p. 401:

“BAT options to achieve these levels:

- For HFO firing with max. 0.3 % N in fuel oil NOx<450 mg/Nm3.

- For HFO firing with max. 0.2 % N in fuel oil NOx<360 mg/Nm3.”

(7)	50 100 mg/Nm³ in case of boilers in SIS and MIS as defined in Directive 2009/72/EC.]

Comment: Based on the experience of the Greek authorities from boilers using HFO with low sulphur content (1%) and low ash content, to gether with electrostatic filters.

*	Further changes may be required to address existing installations and to fully align the text with the provisions of the Gothenburg Protocol, where relevant.

2. Emission limit values (mg/Nm³) for engines and gas turbines

| Pollutant | Type of installation | Liquid fuels | Natural gas | Gaseous fuels other than natural gas |
| --- | --- | --- | --- | --- |
| SO2 | Engines and gas turbines | 60(4) | - | 15 |
| NOX | Engines | 190 (1) (5) | 95 (2) | 190 |
|  | Gas turbines (3) | 75(6) | 50 | 75 |
| Particulate matter | Engines and gas turbines | 10(7) | - | - |

(1)	225 mg/Nm³ for dual fuel engines in liquid mode.

(2)	190 mg/Nm³ for dual fuel engines in gas mode.

(3)	Emission limit values are only applicable above 70 % load.

[(4)	590 mg/Nm³ for diesel engines in SIS and MIS as defined in Directive 2009/72/EC

Comment: According to BREF LCP 2006, in apr.6.1.10.3.2 Control of emissions to air from liquid fuel-fired (diesel) engines / Abatement of SO2 emissions, p. 356:

“The sulphur oxide emission is related to the fuel (proportional to the sulphur content of the fuel). The primary method to reduce the SOx emissions is to use a fuel with a lower sulphur content, whenever commercially available.”

The ELV of 590 mg/Nm3 corresponds the stoichiometrically to low sulphur HFO (1% w.w), i.e. the minimum content that is available in the Greek market.

(5)	1300 mg/Nm³ for diesel engines equal to or below 20 MW and 1850 mg/Nm³ for diesel engines equal to or above 20 MW in SIS and MIS as defined in Directive 2009/72/EC

Comment: The exact wording in the new Goeteborg Protocol for NOx in this case is:

«Where Selective Catalytic Reduction (SCR) cannot currently be applied for technical and logistical reasons like on remote islands or where the availability of sufficient amounts of high quality fuel cannot be guaranteed, a transition period of 10 years after the entry into force of the present Protocol for a Party may be applied for diesel engines and dual fuel engines during which the following ELVs apply:

–	Dual fuel engines: 1,850 mg/m³ in liquid mode; 380 mg/m3 in gas mode.

–	Diesel engines — Slow (< 300 rpm) and Medium (300–1,200 rpm)/speed: 1,300 mg/m³ for engines between 5 and 20 MWth and 1,850 mg/m³ for engines > 20 MWth.

–	Diesel engines — High speed (> 1200 rpm): 750 mg/m³.»

The term “remote islands” is not defined in the EU legislation or in the Protocol. The common understanding is that it is equivalent to SIS/MIS.

The last indent is not relevant to MCPs.

To our knowledge, there are also commercially available technological solutions for 4 strokes engines that go up to 35 MW.

(6)	550 mg/Nm³ in SIS and MIS as defined in Directive 2009/72/EC

Comment: Based on the experience of the Greek authorities on gas turbines that operate with diesel oil without excessive water consumption. Smaller ELVs cannot be attained without significantly higher water consumption. This water is not available in most of SIS/MIS.

(7)	75 mg/Nm³ for diesel engines in SIS and MIS as defined in Directive 2009/72/EC.]

Comment: Based on the experience of Greek authorities on diesel engines that operate with HFO with low ash content. According to BREF LCP 2006, the use of secondary abatement measures for SIS/MIS is not a commercially available option and as primary measure the use of low sulphur and low ash content HFO (1%) is proposed (par. 6.5.5.2 ΒΑΤ for liquid fuel-fired (diesel) engines / Dust and heavy metals emissions). This view is also supported by EUROMOT in the discussions for the revision of relevant LCP BREF.